# Engineering Specification

# Model E3 High Pressure Alarm Check Valve

Recommended CSI MasterFormat Specification Location: 21 13 13, Wet-Pipe Sprinkler Systems (formerly 13930)

Alarm Check Valve shall be [cULus Listed] [FM Approved] for use in wet-pipe fire protection systems for installation in the vertical or horizontal position.  The Alarm Check Valve shall be a straight flow design, check type valve with grooved seat design. The Alarm Check Valve shall have a rated working pressure of 300 psi (20.7 bar) and shall be factory hydrostatic tested at 600 psi (41.4 bar). Valve size shall be [4” (100mm)] [6” (150mm)] [165mm] [8” (200mm)] with grooved end connections per ANSI/AWWA C606.  Valve construction shall be cast iron.  The Alarm Check Valve trim shall be galvanized with [constant pressure closed drain, including external bypass trim] [variable pressure closed retard chamber drain, including external bypass and retard chamber]. Alarm check valve trim shall include a non-silenceable alarm connection for the waterflow pressure switch and shall be configured to cause the clapper to open when testing alarm line devices. {Optional: A [cULus Listed] [FM Approved] pressure relief valve trim kit shall be provided.} [Optional: A Test & Drain valve trim kit shall be provided.]

Alarm Check Valve shall be the Reliable Model E3 High Pressure Alarm Check Valve. Refer to Reliable Bulletin 410 for associated information.