Engineering Specification

Model F1 LO Standard Response Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be a standard response, [standard spray upright] [standard spray pendent] [conventional upright/pendent] [extended coverage pendent] that is [cULus Listed] [FM Approved]. Sprinkler frame and deflector shall be of bronze frame construction having a ¾” NPT thread.  Water seal assembly shall consist of a Teflon-coated Belleville spring washer and top-loaded extruded cup with 3 mm glass bulb containing no plastic parts. Sprinkler temperature rating shall be [135F (57C)] [155F (68C)] [175F (79C)] [200F (93C)] [286F (141C)] [360F (182C)].  Sprinklers shall have a nominal K-factor of 8.0 gpm/psi1/2 (115 l/min/bar1/2) – large orifice. Sprinklers shall have a rated working pressure of 175 psi (12.1 bar).  Standard finish: [Bronze] [Chrome] [Polyester Coated] [Special finish– specify].

Sprinklers shall be of the Model F1 LO Series. Refer to Reliable Bulletin 117 for associated sprinkler identification number (SIN) with respect to style, orifice size and thread combination.

For recessed pendent sprinklers, add:

Recessed escutcheon assembly shall be a two-piece “friction fit” escutcheon with [Model F2 escutcheon: ½” (13 mm)] [Model F1 escutcheon: ¾”(19 mm)] adjustment. Standard finish: [White Painted] [Chrome] [Brass] [Special finish– specify]. The Model F1 escutcheon is the only recessed escutcheon permitted to be used with the Model F1 LO Pendent and EC Sprinklers.

For extended coverage pendent sprinklers, add:

Extended coverage pendent and recessed pendent Model F1 LO sprinklers are available for modifications or additions to existing light hazard sprinkler systems with standard-response sprinklers as well as for replacement of individual standard-response sprinklers in existing light hazard sprinkler systems.