Engineering Specification

Model F1-300 Standard Response Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be a standard response, standard spray [upright] [pendent] [recessed pendent] that is cULus Listed. Sprinkler frame and deflector shall be of bronze frame construction having a ¾” NPT thread.  Water seal assembly shall consist of a Teflon-coated Belleville spring washer and top-loaded extruded cup with 5 mm glass bulb containing no plastic parts. Sprinkler temperature rating shall be [135F (57C)] [155F (68C)] [175F (79C)] [200F (93C)] [286F (141C)] [360F (182C)].  Sprinklers shall have a nominal K-factor of 8.0 gpm/psi1/2 (115 l/min/bar1/2) – large orifice. Sprinklers shall have a rated working pressure of 300 psi (20.7 bar).

Standard finish: [Bronze] [Chrome Plated] [White Polyester] [Special finish– specify].

Sprinklers shall be of the Model F1-300 Series. Refer to Reliable Bulletin 155 for associated sprinkler identification number (SIN) with respect to style, orifice size and thread combination.

For recessed pendent sprinklers, add:

Recessed escutcheon assembly shall be a two-piece “friction fit” escutcheon with ¾” (19 mm) adjustment. Standard finish: [White Painted] [Chrome] [Brass] [Special finish– specify]. The Model F1 escutcheon is the only escutcheon permitted to be used with the Model F1-300 recessed sprinkler.