Engineering Specification

Model F1FR LO Quick Response Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be a quick response, [standard spray upright] [standard spray pendent] [conventional upright/pendent] [standard spray recessed pendent] that is [cULus Listed] [FM Approved]. Sprinkler frame and deflector shall be of bronze frame construction having a ¾” NPT thread.  Water seal assembly shall consist of a Teflon-coated Belleville spring washer and top-loaded extruded cup with 3 mm glass bulb containing no plastic parts. Sprinkler temperature rating shall be [135F (57C)] [155F (68C)] [175F (79C)] [200F (93C)] [286F (141C)].  Sprinklers shall have a nominal K-factor of 8.0 gpm/psi1/2 (115 l/min/bar1/2) – large orifice. Sprinklers shall have a rated working pressure of 175 psi (12.1 bar).  Standard finish: [Bronze] [Chrome Plated] [White Polyester] [Special finish– specify].

Sprinklers shall be of the Model F1FR LO Series. Refer to Reliable Bulletin 136 for associated sprinkler identification number (SIN) with respect to style, orifice size and thread combination.

For recessed pendent sprinklers, add:

Recessed escutcheon assembly shall be a two-piece “friction fit” escutcheon with [Model F2 escutcheon: ½” (13 mm)] [Model F1 escutcheon: ¾”(19 mm)] adjustment. Standard finish: [White Polyester] [Chrome Plated] [Brass] [Special finish– specify].

Recessed escutcheons that are permitted by the manufacturer to be used with each Model F1FR LO recessed sprinkler shall be used.