Engineering Specification

Model F1FR Series Quick Response Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be a quick response, [standard spray upright] [standard spray pendent] [conventional upright/pendent] [vertical sidewall] [horizontal sidewall] that is [cULus Listed] [FM Approved]. Sprinkler frame and deflector shall be of bronze frame construction having a ½” NPT thread.  Water seal assembly shall consist of a Teflon-coated Belleville spring washer and top-loaded extruded cup with 3 mm glass bulb containing no plastic parts. Sprinkler temperature rating shall be [135F (57C)] [155F (68C)] [175F (79C)] [200F (93C)] [286F (141C)].  Sprinklers shall have a nominal K-factor of [2.8 gpm/psi1/2 (40 l/min/bar1/2) – small orifice] [4.2 gpm/psi1/2 (61 l/min/bar1/2) – small orifice] [5.6 gpm/psi1/2 (81 l/min/bar1/2) – standard orifice]. Sprinklers shall have a rated working pressure of 175 psi (12.1 bar).  Standard finish: [Bronze] [Chrome Plated] [White Polyester] [Special finish– specify].

Sprinklers shall be of the Model F1FR Series. Refer to Reliable Bulletin 014 for associated sprinkler identification number (SIN) with respect to style, orifice size and thread combination.

For recessed sprinklers, add:

{Recessed escutcheon assembly shall be a factory-assembled, two-piece steel escutcheon of push-on and thread off design with ½” adjustment. Standard finish shall be [White Polyester] [Chrome Plated] [Brass] [Special finish – specify].} {Recessed escutcheon assembly shall be a two-piece “friction fit” escutcheon with [Model F2 escutcheon: ½” (13 mm)] [Model F1 escutcheon: ¾”(19 mm)] adjustment. Standard finish: [White Polyester] [Chrome Plated] [Brass] [Special finish– specify].}

Recessed escutcheons that are listed for use with each Model F1FR Series recessed sprinkler shall be used.

For concealed pendent sprinklers, add:

Concealed pendent sprinklers shall have a factory-installed, steel sprinkler cup. Method of attaching the cover plate to the sprinkler cup shall be a push-on and thread-off design allowing [1/2” (13 mm)] [5/8” (8 mm)] of adjustment. The cover plate temperature rating shall be [135F (57C)] [165F (74C)].  A factory applied protective cap shall be provided to protect against installation damage. Standard cover plate finish: [Chrome] [White] [Special finish– specify].

Cover plates used with the Model F1FR56 Concealed Pendent and F1FR56LL Concealed Pendent sprinklers shall be the Model CCP cover plate.