Engineering Specification

Model F1FR-300 QREC CCP Series Quick Response

Extended Coverage Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be a quick response, extended coverage pendent that is cULus Listed. Sprinkler frame and deflector shall be of bronze frame construction having a ¾” NPT thread.  Water seal assembly shall consist of a Teflon-coated Belleville spring washer and top-loaded extruded cup with 3 mm glass bulb containing no plastic parts. Sprinkler temperature rating shall be [135F (57C)] [155F (68C)].  Sprinklers shall have a nominal K-factor of 8.0 gpm/psi1/2 (115 l/min/bar1/2) – large orifice. Sprinklers shall have a rated working pressure of 300 psi (20.7 bar).

Concealed pendent sprinklers shall have a factory-installed, steel sprinkler cup. Method of attaching the cover plate to the sprinkler cup shall be a push-on and thread-off design allowing [1/2” (13 mm)] [5/8” (8 mm)] of adjustment. The cover plate temperature rating shall be 135F (57C).  A factory applied protective cap shall be provided to protect against installation damage. Standard cover plate finish: [Chrome] [White] [Special finish– specify].

Cover plates used with the Model F1FR-300 QREC concealed pendent shall be the Model CCP cover plate.

Sprinklers shall be the Model F1FR-300 QREC CCP concealed quick response extended coverage sprinkler, SIN R5942. Refer to Reliable Bulletin 167 for associated sprinkler information.