Engineering Specification

Model F1FR56-300 Series Quick Response Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be a quick response, standard spray [upright] [pendent] [horizontal sidewall] that is cULus Listed. Sprinkler frame and deflector shall be of bronze frame construction having a ½” NPT thread. Water seal assembly shall consist of a Teflon-coated Belleville spring washer and top-loaded extruded cup with 3 mm glass bulb containing no plastic parts. Sprinkler temperature rating shall be [135F (57C)] [155F (68C)] [175F (79C)] [200F (93C)] [286F (141C)].  Sprinklers shall have a nominal K-factor of 5.6 gpm/psi1/2 (81 l/min/bar1/2) – standard orifice. Sprinklers shall have a rated working pressure of 300 psi (20.7 bar).

Standard finish: [Bronze] [Chrome Plated] [White Polyester] [Special finish– specify].

Sprinklers shall be of the Model F1FR56-300 Series. Refer to Reliable Bulletin 026 for associated sprinkler identification number (SIN) with respect to style, orifice size and thread combination.

For recessed sprinklers, add:

{Recessed escutcheon assembly shall be a factory-assembled, two-piece steel escutcheon of push-on/thread-off design with ½” (13 mm) adjustment. Standard finish: [White Polyester] [Chrome Plated] [Brass] [special finish – specify]} {Recessed escutcheon assembly shall be a two-piece “friction fit” escutcheon with [Model F2 escutcheon: ½” (13 mm)] [Model F1 escutcheon: ¾”(19 mm)] adjustment. Standard finish: [White Polyester] [Chrome Plated] [Brass] [Special finish– specify].} Recessed escutcheons that are permitted by the manufacturer to be used with each Model F1FR56-300 Series recessed sprinkler shall be used.

For concealed sprinklers, add:

Concealed pendent sprinklers shall have a factory-installed, steel sprinkler cup. Method of attaching the cover plate to the sprinkler cup shall be a push-on/thread-off design allowing [1/2” (13 mm)] [5/8” (8 mm)] of adjustment. The cover plate temperature rating shall be [135F (57C)] [165F (74C)].  A factory applied protective cap shall be provided to protect against installation damage. Standard cover plate finish: [Chrome] [White] [Special finish – specify]. Cover plates used with the Model F1FR-300 Series concealed sprinklers shall be the Model CCP cover plate.