# Engineering Specification

# Model F1FR80-300 QREC Series Quick Response

# Extended Coverage Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be a quick response, extended coverage [pendent] [horizontal sidewall] that is cULus Listed. Sprinkler frame and deflector shall be of bronze frame construction having a ¾” NPT thread.  Water seal assembly shall consist of a Teflon-coated Belleville spring washer and top-loaded extruded cup with 3 mm glass bulb containing no plastic parts. Sprinkler temperature rating shall be [135F (57C)] [155F (68C)] [SIN RA5962 only: 175F (79C)].  Sprinklers shall have a nominal K-factor of 8.0 gpm/psi1/2 (115 l/min/bar1/2) – large orifice. Sprinklers shall have a rated working pressure of 300 psi (20.7 bar).  Standard finish: [Bronze] [Chrome Plated] [White Polyester] [Special finish– specify].

Sprinklers shall be of the Model F1FR80-300 QREC Series. Refer to Reliable Bulletin 159 for associated sprinkler identification number (SIN) with respect to style, orifice size and thread combination.

For recessed pendent sprinklers, add:

Recessed escutcheon assembly shall be a two-piece “friction fit” escutcheon with ¾”(19 mm) adjustment. Standard finish: [White Polyester] [Chrome Plated] [Brass] [Special finish– specify].

Recessed escutcheons that are listed for use with the Model F1FR80-300 QREC recessed pendent sprinkler shall be used.

For concealed sprinkler, add:

Concealed cover plate shall be push-on/thread off with ½” (13 mm) adjustment. Standard finish: [White Paint] [Chrome Plated] [Special finish– specify].

Cover plates that are listed for use with the Model F1FR80-300 QREC concealed sprinkler shall be used.

For recessed horizontal sidewall sprinklers, add:

Recessed escutcheon assembly shall be a two-piece “friction fit” escutcheon with ½” (13 mm) adjustment. Standard finish: [White Polyester] [Chrome Plated] [Brass] [Special finish– specify].

Recessed escutcheons that are listed for use with the Model F1FR80-300 QREC recessed horizontal sidewall sprinkler shall be used.