Engineering Specification

Model F1FR QREC/CCP

Quick Response Extended Coverage Concealed Sprinkler

Sprinklers shall be[cULus Listed quick response, extended coverage concealed pendent sprinklers, capable of providing a maximum coverage area of 20’x20’ (6.1 m x 6.1 m) for light hazard occupancies, with a minimum spacing requirement of 8 ft. (2.4 m).  Extended coverage horizontal sidewall sprinklers shall be installed in conformance with the manufacturer’s flows and pressures for the listed coverage areas and installed in accordance with the applicable installation standard. Sprinkler frame and deflector shall be of bronze frame construction having a [½”][ ¾”] NPT thread, with brass cover plate and copper alloy retainer flange assembly.  Water seal assembly shall consist of a Teflon-coated Belleville spring washer and top-loaded extruded cup with 3 mm glass bulb containing no plastic parts. Sprinklers shall have a nominal K-factor of [5.6 (81.0)] [8.0 (115.3)]. Sprinkler temperature rating shall be [135 (F (57 (C)] [155(F (68 (C)] with a cover plate temperature rating of 135 (F (57 (C).  Method of attaching the cover plate to the factory-assembled, steel sprinkler cup shall be a push-on and thread-off design allowing  [½” (13 mm)] [5/16” (8 mm)] of adjustment.  Rated working pressure shall be 175 psi (12.1 bar).  A factory applied protective cap shall be provided to protect against installation damage.  Standard cover plate finish to be:  [Chrome] [White] [Specialty – specify]. Quick Response extended coverage concealed sprinkler shall be Reliable Model F1FR QREC/CCP, [SIN R4845 (K= 5.6, ½” NPT)] [SIN R4842 (K= 8.0, ¾” NPT)] (Bulletin 151).