# Engineering Specification

# Model F1Res LL Series Pendent Glass Bulb

# Residential Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 13, Wet-pipe Sprinkler Systems (formerly 13930)

Sprinklers shall be residential type cULus Listed for installation in accordance with NFPA 13, NFPA 13R, and NFPA 13D.  Residential sprinklers shall be installed in conformance with the manufacturer’s installation guidelines and the applicable installation standard. Sprinkler body shall be of bronze alloy construction having [½” NPT] [ISO7-1R1/2] threads.  Thermal element shall consist of a 3mm glass bulb. Sprinkler shall be certified by Underwriters Laboratories, Inc. and Underwriters Laboratories of Canada for health effects to NSF/ANSI Standard 61 Annex G requiring less than 0.25% lead content. Sprinkler K-factors shall be [3.0 gpm/psi1/2 (43.2 l/min/bar1/2)] [4.9 gpm/psi1/2 (70.6 l/min/bar1/2)] [5.8 gpm/psi1/2 (84 l/min/bar1/2)].  Sprinkler temperature classification shall be [Ordinary 155F (68C)] [Intermediate 175°F (79°C)]. Sprinkler finish to be [brass] [white] [chrome] [special – specify].

For recessed sprinklers, add:

Recessed pendent sprinklers shall be installed with listed 2-piece escutcheons offering a minimum of [¾” (12.7mm)] [3.0k only: ½” (12.7mm)] of adjustment. Deflector to be located between [¾” and 1-1/2”] [3.0k only: 15/16” and 1-1/2”] below the ceiling. Escutcheon color to be [brass] [white] [chrome] [special – specify] consistent with sprinkler finish.

For concealed sprinklers, add:

Conical concealed pendent sprinklers to utilize a listed and approved cover plate attached to a factory installed cup. Cover plate must offer a minimum of ½” (12.7mm) of adjustment. Cover plate finish to be [chrome] [white] [special finish – specify].

Residential sprinklers shall be Reliable Model [F1Res 30 LL, SIN RA3311] [F1Res 49 LL, SIN RA3316] [F1Res 58 LL, SIN RA3313].