Engineering Specification

Model F4FR-NF Series Special Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 13, Wet Pipe Sprinkler Systems (formerly 13930)

Sprinklers shall be cULus Listed, non-ferrous, quick response concealed pendent sprinkler specifically designed and tested for use in MRI type applications, and able to withstand exposure to a magnetic field of up to 6 Tesla. Sprinkler to be of bronze frame construction with drop down deflector and [135°F (57C)] [155°F (68C)] a 3 mm glass bulb thermal element. Water seal construction shall utilize Belleville spring seal coated with Teflon film on both sides. Concealed pendent sprinkler shall have a nominal K-factor of 5.6 gpm/psi1/2 (80 l/min/bar1/2) – standard orifice and have ½” NPT (R½) thread. Sprinklers shall have a rated working pressure of 175 psi (12 bar).

Flat cover plate assembly construction shall consist of brass cover plate attached to copper alloy skirt using 135F (57C) ordinary temperature classification solder. Cover plate shall attach to sprinkler cup assembly by a push-on or threaded engagement providing 1/2” (15 mm) of cover plate adjustment.  Cover plate design shall be [Finish (specify)].

Sprinklers shall be the Reliable Model F4FR-NF, Non-Ferrous, Concealed Pendent, SIN RA0212. Refer to Reliable Technical Bulletin 002 for associated sprinkler information.