# Engineering Specification

# Model FCA2 Floor Control Valve Assembly

Recommended CSI MasterFormat Specification Location: 21 13 13, Wet-Pipe Sprinkler Systems (formerly 13930)

Floor Control Valve Assembly shall be cULus Listed for use in wet-pipe fire protection systems for installation in the vertical or horizontal position. The Floor Control Valve Assembly shall be {[1-1/4” (30mm)] [1-1/2” (40mm)] [2” (50mm)] listed for 300 psi (20.7 bar)} {[2½” (65mm)] [3” (80mm)] [4” (100mm)] listed for 250 psi (17.2 bar)} {[6” (150mm)] [8” (200mm)]} working pressure with grooved end connections per ANSI/AWWA C606.

The Floor Control Assembly shall be manufactured as a single preassembled unit and consist of the following:

- Supervised butterfly valve with Nylon-11 coated brass in accordance with ASTM A-536 and an EPDM encapsulated coated disc in accordance with ASTM A-536.

- Spring-loaded check valve with a straight flow design.  Construction to be cast iron with a grooved one-piece bronze seat. Clapper assembly shall be ductile iron casting with brass bushing assembly, EPDM rubber facing seal and stainless-steel clamping ring.  Valve body construction shall consist of gray iron per ASTM-A48 Class 30A.

- Single-handle, tri-position Test & Drain valve allowing both testing of the waterflow alarm and draining of a wet-pipe fire protection system. Test & Drain valve shall be provided with an adjustable pressure relief valve trim kit with 175 to 310 psi (12.1 to 20.4 bar) rating.

- A vane type waterflow switch with non-corrosive insert for use on wet-pipe sprinkler systems utilizing two (2) single pole, double throw, snap action switches and an adjustable, instantly recycling pneumatic retard. Waterflow switch to have an electrical rating of 10A @ 125/250 VAC / 2.5 A @ 24VDC.

Floor Control Valve Assembly shall be the Reliable Model FCA2. Refer to Reliable Bulletin 625 for associated information.