# Engineering Specification

# Model J112 and JL112 Extended Coverage Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be a [quick] [standard] response, extended coverage [pendent] [upright] that is cULus Listed. Sprinkler frame shall be of bronze alloy and the deflector shall be of brass alloy construction having a [¾” NPT] [ISO 7-1R¾] thread.  Water seal assembly shall consist of a Teflon-coated Belleville spring washer and [J112: top-loaded extruded cup with 3 mm glass bulb] [JL112: beryllium-nickel fusible solder link assembly, utilizing a strut and lever principal of operation] containing no plastic parts. Sprinkler temperature rating shall be [155F (68C)] [165F (74C)] [200F (93C)] [212F (100C)] [286F (141C)].  Sprinklers shall have a nominal K-factor of 11.2 gpm/psi1/2 (160 l/min/bar1/2) – extra-large orifice. Sprinklers shall have a rated working pressure of 175 psi (12 bar).  Standard finish: [Bronze] [Chrome Plated] [White Polyester] [Special finish – Specify].

Sprinklers shall be of the Model [J112] [JL112] Series. Refer to Reliable Bulletin 172 for associated sprinkler identification number (SIN) with respect to style, orifice size and thread combination.

For recessed sprinklers, add:

{Recessed escutcheon assembly shall be a factory-assembled, two-piece steel escutcheon of push-on and thread off design with ½” adjustment. Standard finish shall be [White Polyester] [Chrome Plated] [Brass] [special finish – specify].} {Recessed escutcheon assembly shall be a two-piece “friction fit” escutcheon with [Model F2 escutcheon: ½” (13 mm)] [Model F1 escutcheon: ¾”(19 mm)] adjustment. Standard finish: [White Polyester] [Chrome Plated] [Brass] [Special finish– specify].}

Recessed escutcheons that are listed for use with the Model [J112] [JL112] recessed sprinkler shall be used.

For Specific Application Criteria for Use Under Concrete Tee Construction, add:

Pendent and upright sprinklers shall be cULus Listed for installation under concrete tee construction in accordance with the following specific application criteria:

- Max. Tee Depth: 2’- 6” (0.8m)

- Max. Tee Stem Spacing: 7’- 6” (2.3m)

- Min. Tee Stem Spacing: 3’- 0” (0.9m)

- Max. Tee Length: 32’- 0” (9.8m) or baffles not less than the depth of the tees must be installed so that the longitudinal space between baffles does not exceed 32ft (9.8m) in length.

- Max. Deflector distance below Tee: 1” (25mm)

- Comply with obstructions to the Sprinkler Discharge Pattern Development requirements of the NFPA13 where deflector is located above bottom of tee.