# Engineering Specification

# Model J168 Upright Standard Response Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be standard response upright sprinklers that are [FM Approved] [cULus Listed]. Sprinkler construction shall be a bronze, die-cast frame with grooved wrench flat and copper-alloy deflector. Water seal assembly shall consist of a Teflon-coated Belleville spring washer containing no plastic parts, utilizing a levered fusible alloy solder link. Sprinkler temperature rating shall be [165F (74C)] [212F (100C)] [286F (141C)].  Sprinklers shall have a nominal K-factor of 16.8 gpm/psi1/2 (242 l/min/bar1/2) and [¾” NPT] [ISO 7-1R¾] thread. Sprinklers shall have a rated working pressure of 175 psi (12 bar) and factory tested to 500 psi (34.5 bar).

{Special Application Finishes Option:

Exposed sprinklers subject to corrosive atmospheres shall have a factory-applied [165 ºF (74ºC) clear wax-coated] [212 ºF (100 ºC) brown wax-coated] [lead plated for 165 F (74 C), 212F (100 C), or 286F (141C)] [wax-coated over lead plated] corrosion resistant coating.}

Sprinklers shall be the Reliable Model J168 upright sprinklers. Refer to Reliable Bulletin 011 for associated sprinkler information.