Engineering Specification

Model KFR80 Quick Response Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be a quick response standard spray [upright] [pendent] that is [cULus Listed] [FM Approved].  Sprinkler frame and deflector shall be of brass frame construction having a ¾” NPT thread.  Water seal assembly shall consist of an approved beryllium-nickel fusible solder link assembly, utilizing a strut and lever principal of operation, with Teflon-coated nickel sealing washer and bronze alloy cap containing no plastic parts.  Sprinkler temperature rating shall be [165F (74C)] [212F (100C)].  Sprinklers shall have a nominal K-factor of 8.0 gpm/psi1/2 (115 l/min/bar1/2) – large orifice.  Sprinklers shall have a rated working pressure of [175 psi (12.1 bar) for FM Approved] [250 psi (17.2 bar) for UL Listed].  Standard finish shall be [Bronze] [Chrome Plated] [White Polyester] [Special finish – specify].

Sprinklers shall be of the Model KFR80 Series. Refer to Reliable Bulletin 054 for associated sprinkler identification number (SIN) with respect to style.

## For recessed pendent, add:

{Recessed escutcheon assembly shall be a factory-assembled, two-piece steel escutcheon of push-on and thread off design with ½” adjustment. Standard finish shall be [White Polyester] [Chrome Plated] [Brass] [special finish – specify].} {Recessed escutcheon assembly shall be a two-piece “friction fit” escutcheon with ½” adjustment. Standard finish: [White Polyester] [Chrome Plated] [Brass] [Special finish– specify].}

Recessed escutcheons that are permitted to be used with each Model KFR80 Series recessed sprinkler shall be used.