# Engineering Specification

# Model MV Medium Velocity Directional Spray Nozzles

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Nozzles shall be cULus Listed non-automatic, fixed pattern, medium velocity directional spray nozzles. Nozzle frames and internal deflectors shall be of brass construction having [½” NPT] [ISO 7-1 R1/2] threads. Optional blow-off plugs shall have identification marks with respect to the nozzle K-factor. Nozzles shall have a nominal K-factor of [1.2 gpm/psi1/2 (17 l/min/bar1/2)] [1.8 gpm/psi1/2 (26 l/min/bar1/2)] [2.3 gpm/psi1/2 (33 l/min/bar1/2)] [3.0 gpm/psi1/2 (43 l/min/bar1/2)] [4.1 gpm/psi1/2 (59 l/min/bar1/2)] [5.6 gpm/psi1/2 (81 l/min/bar1/2)] [7.2 gpm/psi1/2 (104 l/min/bar1/2)].  Nozzle shall feature an internal deflector and deflector angles shall be 65°, 80°, 95°, 110°, 125°, 140°, 160°, or 180°. Nozzle shall have a rated working pressure of 175 psi (12.1 bar).  Nozzle finish shall be [Brass] [Electroless Nickel PTFE (ENT)]. Manufacturer shall provide AutoCAD three-dimensional (3D) representations of nozzle spray patterns to facilitate placement of nozzles and review of the fire protection shop drawings.

Nozzles shall be Reliable Model MV Series. Refer to Reliable Bulletin 106 for associated information.