# Engineering Specification

# Model P25 ESFR Pendent Automatic Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Sprinklers shall be Early Suppression Fast Response (ESFR) pendent suppression mode sprinklers FM Approved as quick-response storage and non-storage sprinklers.  Sprinkler frame and deflector to be of bronze construction. ESFR sprinkler shall be short and compact with a height of 2-7/8” (72 mm) and a diameter of 2” (52 mm). Fusible alloy solder link assembly shall utilize the strut and lever principle of operation with approved fast response beryllium-nickel thermal element with protective [black painted, 165ºF (74ºC)] [gray painted, 212ºF (100ºC)] coating. Water seal shall consist of a Teflon-coated Bellville spring washer and brass cap assembly containing no plastic parts.  ESFR sprinklers shall have a nominal K-factor of 25.2 gpm/psi1/2 (360 l/min/bar1/2) and [1” NPT threaded] [ISO7 R-1 threaded] end connections.  Sprinklers shall have a rated working pressure of 175 psi (12 bar). Sprinkler temperature rating shall be [Ordinary 165ºF (74ºC)] [Intermediate 212ºF (100ºC)].  ESFR pendent sprinklers shall be Reliable Model P25, SIN R602. Refer to Reliable Bulletin 070 for associated sprinkler information.