Engineering Specification

Models A and B Automatic Pressure Maintenance Devices

Recommended CSI MasterFormat Specification Location: 21 13 00, Fire Suppression Sprinkler Systems (formerly 13930)

Model A

[cULus Listed] [FM Approved] regulating-type air pressure maintenance device shall be capable of maintaining a constant system pressure, automatically, regardless of any pressure fluctuations from the compressed air or nitrogen source. The pressure maintenance device shall be constructed of galvanized trim and brass parts.  The device shall consist of ¼” supply bypass piping and a ½” section of piping for rapid restoration of system pneumatic pressure.  The ¼” bypass piping shall contain shutoff valves, a strainer, a check valve and a field adjustable pressure regulator.  The pressure regulator shall have an adjustable outlet pressure range of 5 to 75 psi (.34 to 5.2 bar).  The ½” section of piping shall contain a ball valve for rapid restoration of system pressure and associated trim for connection to the dry pipe valve system air supply line.  The assembly shall have a working pressure rating of 175 psi (12.1 bar).  The pressure maintenance device shall be the Reliable Model A. Refer to Reliable Bulletin 251 for associated information.

Model B

For use in conjunction with a tankless air compressor without a start/stop pressure control switch to maintain the correct air pressure in a dry pipe valve, dry pilot line, or a deluge valve based preaction system.  Pressure switch shall be factory set to start the compressor at 29 psi (2.0 bar) and stop the compressor at 35 psi (2.4 bar). The pressure switch shall have an adjustment range between 14 – 60 psi (1.0 – 4.1 bar).  Maximum inlet pressure not to exceed 175 psi (12 bar).  Inlet and Outlet end connections to be female ½” NPT.

The [cULus Listed] [FM Approved] pressure maintenance device shall have an attached pressure control switch capable of maintaining system pressure, automatically, between the set cut-in and cut-out pressure of the pressure switch. The pressure maintenance device shall be constructed of galvanized trim and brass parts.  The device shall consist of ¼” supply bypass piping and a ½” section of piping for rapid restoration of system pneumatic pressure.  The ¼” bypass piping shall contain shutoff valves, a strainer, a check valve and a field adjustable pressure switch.  The pressure regulator shall have an adjustable outlet pressure range of 5 to 50 psi (.34 to 3.4 bar).  The ½” section of piping shall contain a ball valve for rapid restoration of system pressure and associated trim for connection to the dry pipe valve system air supply line.  The assembly shall have a working pressure rating of 175 psi (12.1 bar). The pressure maintenance device shall be the Reliable Model B. Refer to Reliable Bulletin 251 for associated information.