# Engineering Specification

# Model RFC Series Flat Cover Plate Concealed

# Residential Pendent Sprinklers

Recommended CSI MasterFormat Specification Location: 21 13 13, Wet-pipe Sprinkler Systems (formerly 13930)

Sprinklers shall be flat cover plate concealed residential pendent sprinklers that are cULus Listed for installation in accordance with NFPA 13, NFPA 13R, and NFPA 13D. Residential sprinklers shall be installed in conformance with the manufacturer’s installation guidelines and the applicable installation standard. Sprinklers shall have a drop-down deflector secured on pins. Sprinkler body shall be of brass alloy construction having [½” NPT] [ISO7-1R1/2] [7.6K sprinklers only: ¾” NPT] [ISO7-1R3/4] threads.  Thermal element shall consist of a nickel alloy fusible solder link. Sprinkler K-factors shall be [3.0 gpm/psi1/2 (43.2 l/min/bar1/2)] [4.3 gpm/psi1/2 (62 l/min/bar1/2)] [4.9 gpm/psi1/2 (70.6 l/min/bar1/2)] [5.8 gpm/psi1/2 (84 l/min/bar1/2)] [7.6 gpm/psi1/2 (109 l/min/bar1/2)]. Sprinkler temperature classification shall be [Ordinary 165F (74C) with 135F (57C) temperature rated cover plate] [Intermediate 212°F (100°C) with 165°F (74°C) temperature rated cover plate].

Cover plate assembly shall consist of a brass cover plate and copper alloy retainer flange having a push-on and thread-off design allowing a minimum of ½” (13 mm) cover plate adjustment.  Any secure engagement between the cover plate and the cup shall assure that the drop-down deflector is properly located below the ceiling.  Sprinkler installation should be achieved without removal of the plastic cap to protect the sprinkler from damage. Cover plate finish shall be: [White] [Chrome] [Special Application – specify].

Residential flat cover plate concealed pendent sprinklers shall be Reliable Model [RFC30, SIN RA0611] [RFC43, SIN RA0612] [RFC49, SIN RA0616] [RFC58, SIN RA0613] [RFC76, SIN RA0618].